1. **GENERAL DATA AND INFORMATION:**

|  |  |  |  |
| --- | --- | --- | --- |
| Phase | CT No. | Serial Number | Function |
| R |  |  |  |
| Y |  |  |  |
| B |  |  |  |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| CT No. | Ratio | CLASS | VKP | Im | RCT @ 75°C | Burden (VA) |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |

1. **PRIMARY WITH GROUND**

**APPLIED VOLTAGE : 1KV – 1 min**

|  |  |
| --- | --- |
| PHASE | INSULATION RSISTANCE MEASURED |
| R |  |
| Y |  |
| B |  |

1. **PRIMARY WITH SECONDARY**

**APPLIED VOLTAGE : 500V – 1 min**

|  |  |  |  |
| --- | --- | --- | --- |
| CT No. | INSULATION RSISTANCE MEASURED | | |
| R | Y | B |
|  |  |  |  |
|  |  |  |  |
|  |  |  |  |

1. **SECONDARY WITH GROUND**

**APPLIED VOLTAGE : 250V – 1 min**

|  |  |  |  |
| --- | --- | --- | --- |
| CT No. | INSULATION RSISTANCE MEASURED | | |
| R | Y | B |
|  |  |  |  |
|  |  |  |  |
|  |  |  |  |

CRITERIA:

Primary to ground & primary to secondary : >1 GΩ

Secondary to ground & secondary to secondary : >100 MΩ