- GENERAL DATA AND INFORMATION.

| Type: | MiCOM P740 | Rated Current: | 1.00 A |
| --- | --- | --- | --- |
| Make : | ALSTOM | Rated Voltage: | 125 V |
| Firmware Ver.: | E2.1_A | Aux. Voltage: | 48 – 250 V (125 V) |
|  |  | Rated Freq.: | 60 Hz |
|  |  | No. of PU : | 15 |

- MECHANICAL CHECK AND VISUAL INSPECTION

| S.No | DESCRIPTION | REMARKS |
| --- | --- | --- |
| 1 | Inspect for physical damage / defects. |  |
| 2 | Verify connections as per approved drawing. |  |
| 3 | Check tightness of all connections. |  |

- ELECTRICAL TEST.

FUNCTION TEST

| S.No | DESCRIPTION | REMARKS |
| --- | --- | --- |
| 1 | Case Earthing checked. |  |
| 2 | Front Communication verified by software. |  |
| 3 | Set date and time. |  |
| 4 | Binary inputs checked as per schematic. |  |
| 5 | Binary outputs checked as per schematic. |  |
| 6 | LED indications checked. |  |
| 7 | Test switch function verified. |  |
| 8 | Auxiliary DC supply checked. |  |
| 9 | CT circuit checked. |  |

- INPUTS, OUTPUTS AND LEDs CHECK FOR CENTRAL UNIT AND BAY UNIT:

4.1 CENTRAL UNIT

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | K2-K1 | Z1A IN SERVICE |  |
| OC 02 | K4-K3 | Z2A IN SERVICE |  |
| OC 03 | K6-K5 | SPARE |  |
| OC 04 | K8-K7 | SPARE |  |
| OC 05 | K10-K9 | SPARE |  |
| OC 06 | K12-K11 | SPARE |  |
| OC 07 | K14-K13 | SPARE |  |
| OC 08 | K16-K15 | SPARE |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

CENTRAL UNIT LEDS:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | PHASE A OPTD |  | FnkeyLED 01 | Green: CZ NO Alarm Red: circuitry fault blocking Yellow : circuitry fault alarm |  |
| LED 02 | PHASE B OPTD |  | FnkeyLED 02 | Green: CZ NO Alarm Red :PU circuitry fault blocking Yellow :PU circuitry fault alarm |  |
| LED 03 | PHASE C OPTD |  | FnkeyLED 03 | SPARE |  |
| LED 04 | Green:87BB Z1 OPTD Red:50BF Z1 OPTD Yellow :Both |  | FnkeyLED 04 | Green :NO ALARM Red :Z1-87BB BLOKED Yellow :Z1-87BB &50BF BLOKED |  |
| LED 05 | Green:87BB Z2 OPTD Red :50BF Z2 OPTD Yellow :Both |  | FnkeyLED 05 | Green :NO ALARM Red :Z2-87BB BLOKED Yellow :Z2-87BB &50BF BLOKED |  |
| LED 06 | Green: Z1 healthy Red:Z1 Blocking Yellow :CZ Blocking |  | FnkeyLED 06 | SPARE |  |
| LED 07 | Green: Z2 healthy Red : Z2 Blocking Yellow: CZ Blocking |  | FnkeyLED 07 | Check Zone ALARM |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION CU & PU |  |

4.2: BAY UNITS:-

BAY Name:   PU07 (BC-2A_ D130)(130B)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | C2-C1 | CB 130 OPEN |  |
| OC 02 | C4-C3 | CB 130 CLOSE |  |
| OC 03 | C6-C5 | DS 134 OPEN |  |
| OC 04 | C8-C7 | DS 134 CLOSE |  |
| OC 05 | C10-C9 | DS 136 OPEN |  |
| OC 06 | C12-C11 | DS 136 CLOSE |  |
| OC 07 | C14-C13 | CBF INITI |  |
| OC 08 | C16-C15 | Spare |  |
| OC 09 | A2-A1 | Spare |  |
| OC 10 | A4-A3 | Spare |  |
| OC 11 | A6-A5 | Spare |  |
| OC 12 | A8-A7 | Spare |  |
| OC 13 | A10-A9 | Spare |  |
| OC 14 | A12-A11 | Spare |  |
| OC 15 | A14-A13 | Spare |  |
| OC 16 | A16-A15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 134 CLOSE/OPEN |  | FnkeyLED 01 | SPARE |  |
| LED 02 | DS 136 CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 130 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF IN |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:   PU08 (BC-1A_D130) (130A)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 130 OPEN |  |
| OC 02 | B4-B3 | CB 130 CLOSE |  |
| OC 03 | B6-B5 | DS 134 OPEN |  |
| OC 04 | B8-B7 | DS 134 CLOSE |  |
| OC 05 | B10-B9 | DS 136 OPEN |  |
| OC 06 | B12-B11 | DS 136 CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 134 CLOSE/OPEN |  | FnkeyLED 01 | OC PHASE A OPTD |  |
| LED 02 | DS 136 CLOSE/OPEN |  | FnkeyLED 02 | OC PHASE B OPTD |  |
| LED 03 | CB 130 CLOSE/OPEN |  | FnkeyLED 03 | OC PHASE C OPTD |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | OC START |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | OC OPTD |  |
| LED 07 | CBF INITI |  | FnkeyLED 07 | EF START |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | EF OPTD |  |
| Fnkey 09LED | CBF from CU |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:       PU09 (BS-2B_D220) (220B)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 220 OPEN |  |
| OC 02 | B4-B3 | CB 220 CLOSE |  |
| OC 03 | B6-B5 | DS 226A OPEN |  |
| OC 04 | B8-B7 | DS 226A CLOSE |  |
| OC 05 | B10-B9 | DS 226B OPEN |  |
| OC 06 | B12-B11 | DS 226B CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 226A CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 226B CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 220 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

4.2: BAY Name:   PU10 (BS-1B D120)(120B)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 120 OPEN |  |
| OC 02 | B4-B3 | CB 120 CLOSE |  |
| OC 03 | B6-B5 | DS 124A OPEN |  |
| OC 04 | B8-B7 | DS 124A CLOSE |  |
| OC 05 | B10-B9 | DS 124B OPEN |  |
| OC 06 | B12-B11 | DS 124B CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 124A CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 124B CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 120 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:   PU11 (D01)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 105 OPEN |  |
| OC 02 | B4-B3 | CB 105 CLOSE |  |
| OC 03 | B6-B5 | DS 104 OPEN |  |
| OC 04 | B8-B7 | DS 104 CLOSE |  |
| OC 05 | B10-B9 | DS 106 OPEN |  |
| OC 06 | B12-B11 | DS 106 CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 104 CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 106 CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 105 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:    PU12 (D03)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 305 OPEN |  |
| OC 02 | B4-B3 | CB 305 CLOSE |  |
| OC 03 | B6-B5 | DS 304 OPEN |  |
| OC 04 | B8-B7 | DS 304 CLOSE |  |
| OC 05 | B10-B9 | DS 306 OPEN |  |
| OC 06 | B12-B11 | DS 306 CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 304 CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 306 CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 305 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:     PU13 (D05)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 505 OPEN |  |
| OC 02 | B4-B3 | CB 505 CLOSE |  |
| OC 03 | B6-B5 | DS 504 OPEN |  |
| OC 04 | B8-B7 | DS 504 CLOSE |  |
| OC 05 | B10-B9 | DS 506 OPEN |  |
| OC 06 | B12-B11 | DS 506 CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 504 CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 506 CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 505 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:    PU14 (D07)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 705 OPEN |  |
| OC 02 | B4-B3 | CB 705 CLOSE |  |
| OC 03 | B6-B5 | DS 704 OPEN |  |
| OC 04 | B8-B7 | DS 704 CLOSE |  |
| OC 05 | B10-B9 | DS 706 OPEN |  |
| OC 06 | B12-B11 | DS 706 CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 704 CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 706 CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 705 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:     PU15 (D09)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 905 OPEN |  |
| OC 02 | B4-B3 | CB 905 CLOSE |  |
| OC 03 | B6-B5 | DS 904 OPEN |  |
| OC 04 | B8-B7 | DS 904 CLOSE |  |
| OC 05 | B10-B9 | DS 906 OPEN |  |
| OC 06 | B12-B11 | DS 906 CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 904 CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 906 CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 905 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:  PU16 (D11)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 1105 OPEN |  |
| OC 02 | B4-B3 | CB 1105 CLOSE |  |
| OC 03 | B6-B5 | DS 1104 OPEN |  |
| OC 04 | B8-B7 | DS 1104 CLOSE |  |
| OC 05 | B10-B9 | DS 1106 OPEN |  |
| OC 06 | B12-B11 | DS 1106 CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 1104 CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 1106 CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 1105 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:         PU17(D13)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 1305 OPEN |  |
| OC 02 | B4-B3 | CB 1305 CLOSE |  |
| OC 03 | B6-B5 | DS 1304 OPEN |  |
| OC 04 | B8-B7 | DS 1304 CLOSE |  |
| OC 05 | B10-B9 | DS 1306 OPEN |  |
| OC 06 | B12-B11 | DS 1306 CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 1304 CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 1306 CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 1305 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

BAY Name:       PU18 (D15)

| Binary Inputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- |
| OC 01 | B2-B1 | CB 1505 OPEN |  |
| OC 02 | B4-B3 | CB 1505 CLOSE |  |
| OC 03 | B6-B5 | DS 1504 OPEN |  |
| OC 04 | B8-B7 | DS 1504 CLOSE |  |
| OC 05 | B10-B9 | DS 1506 OPEN |  |
| OC 06 | B12-B11 | DS 1506 CLOSE |  |
| OC 07 | B14-B13 | CBF INIT |  |
| OC 08 | B16-B15 | Spare |  |
| OC 09 | C2-C1 | Spare |  |
| OC 10 | C4-C3 | Spare |  |
| OC 11 | C6-C5 | Spare |  |
| OC 12 | C8-C7 | Spare |  |
| OC 13 | C10-C9 | Spare |  |
| OC 14 | C12-C11 | Spare |  |
| OC 15 | C14-C13 | Spare |  |
| OC 16 | C16-C15 | Spare |  |
| OC 17 | D2-D1 | Spare |  |
| OC 18 | D4-D3 | Spare |  |
| OC 19 | D6-D5 | Spare |  |
| OC 20 | D8-D7 | Spare |  |
| OC 21 | D10-D9 | Spare |  |
| OC 22 | D12-D11 | Spare |  |
| OC 23 | D14-D13 | Spare |  |
| OC 24 | D16-D15 | Spare |  |

| Binary Outputs | Terminals | Function (Duty) | Checked | Binary Outputs | Terminals | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RL01 | F2-F1 | Spare |  | RL09 | E2-E1 | Spare |  |
| RL02 | F4-F3 | Spare |  | RL10 | E4-E3 | Spare |  |
| RL03 | F6-F5 | Spare |  | RL11 | E6-E5 | Spare |  |
| RL04 | F8-F7 | Spare |  | RL12 | E8-E7 | Spare |  |
| RL05 | F10-F9 | Spare |  | RL13 | E10-E9 | Spare |  |
| RL06 | F12-F11 | Spare |  | RL14 | E12-E11 | Spare |  |
| RL07 | F15-F14(N/O) F15-F13(N/C) | Spare |  | RL15 | E15-E14(N/O) E15-E13(N/C) | Spare |  |
| RL08 | F18-F17(N/O) D18-D16(N/C) | Spare |  | RL16 | E18-E17(N/O) D18-D16(N/C) | Spare |  |

Bay Unit LEDs:

| LED’S | Function (Duty) | Checked | LED’S | Function (Duty) | Checked |
| --- | --- | --- | --- | --- | --- |
| LED 01 | DS 1504 CLOSE/OPEN |  | FnkeyLED 01 | CBF from CU |  |
| LED 02 | DS 1506 CLOSE/OPEN |  | FnkeyLED 02 | SPARE |  |
| LED 03 | CB 1505 CLOSE/OPEN |  | FnkeyLED 03 | SPARE |  |
| LED 04 | 87BB Trip |  | FnkeyLED 04 | IMAGE ALARM |  |
| LED 05 | CBF TRIP |  | FnkeyLED 05 | SPARE |  |
| LED 06 | CT Fail |  | FnkeyLED 06 | SPARE |  |
| LED 07 | CBF INIT |  | FnkeyLED 07 | SPARE |  |
| LED 08 | FIBER COMM ERROR |  | FnkeyLED 08 | SPARE |  |
| Fnkey 09LED | SPARE |  | FnkeyLED 10 | RESET INDICATION |  |

SECONDARY INJECTION TEST:

5.1: CHECK OF THE INPUT CURRENT TRANSFORMERS.

- Measurements are taken as per Bus Zone selection by relative Disconnector closing in the bay.

| BAY NO. | CT RATIO [A] | CURRENT INJECTED [A] |  |  | CURRENT MEASURED in CU [A] |  |  | CURRENT MEASURED in PU [A] |  |  |  | ISOLATOR | MEAS. ZONES |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Rph | Yph | Bph | Rph | Yph | Bph | Rph | Yph | Bph | IN |  |  |
| D130-1A | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | BOTH&CB | Z1A |
| D130-2A | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | BOTH&CB | Z2A |
| D120-1B | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | BOTH&CB | Z1A |
| D120-2B | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | BOTH&CB | Z2A |
| D01 | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 104 | Z1A |
|  |  | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 106 | Z2A |
| D03 | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 304 | Z1A |
|  |  | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 306 | Z2A |
| D05 | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 504 | Z1A |
|  |  | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 506 | Z2A |
| D07 | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 704 | Z1A |
|  |  | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 706 | Z2A |
| D09 | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 904 | Z1A |
|  |  | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 906 | Z2A |
| D11 | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 1104 | Z1A |
|  |  | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 1106 | Z2A |
| D13 | 4000/1 | 0.5 |  |  |  |  |  |  |  |  |  | 7 | Z3 |
|  |  | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 1304 | Z1A |
|  |  | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 1306 | Z2A |
| D15 | 4000/1 | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 1504 | Z1A |
|  |  | 0.5 | 0.75 | 1 |  |  |  |  |  |  |  | 1506 | Z2A |

5.2: ID>1 THRESHOLD (CIRCUITRY FAULT CURRENT) TEST

ID>1 	=   100    A

tID>1	=    3    s

K ID>1 	= 30%

- Set ID>1 alarm timer to 100 ms.

- Applied a current on R phase of each PU and increase the current till appear the circuitry fault alarm. (Output relay of CU “circuitry fault”)

- Repeat the same for Y & B phase.

- Measure the ID>1 Alarm as per the setting.

| BAY NO. | CT RATIO [A] | ID>1 Set Value[A] | tID>1 Set[Sec] | Measured pickup Value [A] |  |  | Measured Time at 2* I D>1 [Sec] |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | R, Y, B | R, Y, B | Rph | Yph | Bph | Rph | Yph | Bph |
| D130-1A | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D130-2A | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D120-1B | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D220-2B | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D01 | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D03 | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D05 | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D07 | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D09 | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D11 | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D13 | 4000/1 | 100 | 3 |  |  |  |  |  |  |
| D15 | 4000/1 | 100 | 3 |  |  |  |  |  |  |

5.3: ID>2 THRESHOLD (TRIPPING CURRENT) TEST:

ID>2 	=  48000 A

K2      =   60%

Applied a current on R phase of each PU and increase the current until the trip of PU

Repeat the same for Y & B phase.

- Measure the tripping Time.

- The tripping time is less than one cycle (<20 ms).

| Panel Ref/ Bay No | CT RATIO [A/A] | ID>2 Primary (A) | ID>2 Setting Calculated Sec.value (A) | Measured Pickup Value [A] |  |  | Measured Time at 2*ID>2 Pickup Value [ms] |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Rph | Yph | Bph | Rph | Yph | Bph |
| D130-1A | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D130-2A | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D120-1B | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D220-2B | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D01 | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D03 | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D05 | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D07 | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D09 | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D11 | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D13 | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |
| D15 | 4000/1 | 4800 | 1.2 |  |  |  |  |  |  |

5.4: TEST OF ISOLATOR ALARM OPTIONS.

| Panel Ref/ Bay No | Q1 Alarm | Q2 Alarm | CB Alarm |
| --- | --- | --- | --- |
| D130-1A |  |  |  |
| D130-2A |  |  |  |
| D120-1B |  |  |  |
| D220-2B |  |  |  |
| D01 |  |  |  |
| D03 |  |  |  |
| D05 |  |  |  |
| D07 |  |  |  |
| D09 |  |  |  |
| D11 |  |  |  |
| D13 |  |  |  |
| D15 |  |  |  |

5.5. -BUS BAR PROTECTION SLOPE TEST:

I Diff

K2 = KCZ

ID>2 = IDCZ>2

K1

ID>1

I Bias

Ibias =    A

- Inject the current as per the following:

I1 => on R Phase of PU No. 1

I2 => on R phase of PU No.2

- By using ramping technique, increase current in one bay and decrease in the other until get the diff value.

- Idiff > ( K2 * Ibias ), Idiff > (KCZ * Ibais )

- Idiff > ( ID>2), Idiff (IDCZ>2 )

IDCZ>2

=

ID>2

Ibias =

KCZ

K2

- Idiff > K x Ibias

- Idiff > Id>2

I Bias  = I1 + I 2

I Diff  =   I1 – I 2

Slope K = I Diff operated / I Bias.

- Discrimination zone slop testing-

| Phase | D05/ PU13 | D13/ PU17 | Ibias | EXP. Idiff | Operated Idiff ZONE 1A DS Q1 close | Operated Idiff ZONE 2A DS Q2 close |
| --- | --- | --- | --- | --- | --- | --- |
| CT Ratio | 4000/1 | 4000/1 |  |  |  |  |
| PH-R | 1 | 1 | 2 | 1.2 |  |  |
| PH-R | 1.5 | 1.5 | 3 | 1.8 |  |  |
| PH-R | 2 | 2 | 4 | 2.4 |  |  |

| Phase | D05/ PU13 | D13/ PU17 | Ibias | EXP. Idiff | Operated Idiff ZONE 1A DS Q1 close | Operated Idiff ZONE 2A DS Q2 close |
| --- | --- | --- | --- | --- | --- | --- |
| CT Ratio | 4000/1 | 4000/1 |  |  |  |  |
| PH-Y | 1 | 1 | 2 | 1.2 |  |  |
| PH-Y | 1.5 | 1.5 | 3 | 1.8 |  |  |
| PH-Y | 2 | 2 | 4 | 2.4 |  |  |

| Phase | D05/ PU13 | D13/ PU17 | Ibias | EXP. Idiff | Operated Idiff ZONE 1A DS Q1 close | Operated Idiff ZONE 2A DS Q2 close |
| --- | --- | --- | --- | --- | --- | --- |
| CT Ratio | 4000/1 | 4000/1 |  |  |  |  |
| PH-B | 1 | 1 | 2 | 1.2 |  |  |
| PH-B | 1.5 | 1.5 | 3 | 1.8 |  |  |
| PH-B | 2 | 2 | 4 | 2.4 |  |  |

- Check  zone slop testing-

| Phase | D05/ PU13 | D13/ PU17 | Ibias | EXP. Idiff | Operated Idiff |
| --- | --- | --- | --- | --- | --- |
| CT Ratio | 4000/1 | 4000/1 |  |  |  |
| PH-R | 2 | 2 | 4 | 1.2 |  |
| PH-R | 3 | 3 | 6 | 1.8 |  |
| PH-R | 3.5 | 3.5 | 7 | 2.1 |  |

| Phase | D05/ PU13 | D13/ PU17 | Ibias | EXP. Idiff | Operated Idiff |
| --- | --- | --- | --- | --- | --- |
| CT Ratio | 4000/1 | 4000/1 |  |  |  |
| PH-Y | 2 | 2 | 4 | 1.2 |  |
| PH-Y | 3 | 3 | 6 | 1.8 |  |
| PH-Y | 3.5 | 3.5 | 7 | 2.1 |  |

| Phase | D05/ PU13 | D13/ PU17 | Ibias | EXP. Idiff | Operated Idiff |
| --- | --- | --- | --- | --- | --- |
| CT Ratio | 4000/1 | 4000/1 |  |  |  |
| PH-B | 2 | 2 | 4 | 1.2 |  |
| PH-B | 3 | 3 | 6 | 1.8 |  |
| PH-B | 3.5 | 3.5 | 7 | 2.1 |  |

5.6 BREAKER FAIL PROTECTION

Breaker Failure Protection: Pickup & Drop-off & Timing Test for external initiation

Settings: T3,4=150ms        I<=0.1 A

| PU No. | Phase | Circuit Breaker Failure |  |  |  |  | Relay LED | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | I Set (A) | P/U (A) | D/O (A) | Stg – 4 (m sec) | Inter trip from other PU(m sec) |  |  |
| PU7 D130B (2A) | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU8 D130A (1A) | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU9 D220B (2B) | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU10 D120B (1B) | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU11 D01 | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU12 D03 | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU13 D05 | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU14 D07 | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU15 D09 | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU16 D11 | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU17 D13 | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |
| PU18 D15 | R | 0.1 |  |  |  |  | CBF |  |
|  | Y |  |  |  |  |  | CBF |  |
|  | B |  |  |  |  |  | CBF |  |

5.6 BREAKER FAIL PROTECTION

Breaker Failure Protection: Pickup & Drop-off & Timing Test for Internal initiation

Settings: T2=150ms        I<=0.1 A

| PU No. | Phase |  |  | Circuit Breaker Failure |  | Relay LED | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | I Set (A) | BB-TRIP (m sec) |  | Stg – 2 (m sec) |  |  |
| PU7 D130B (2A) | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU8 D130A (1A) | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU9 D220B (2B) | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU10 D120B (1B) | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU11 D01 | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU12 D03 | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU13 D05 | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU14 D07 | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU15 D09 | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU16 D11 | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU17 D13 | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |
| PU18 D15 | R | 0.1 |  |  |  | CBF |  |
|  | Y |  |  |  |  | CBF |  |
|  | B |  |  |  |  | CBF |  |

5.7. TOPOLOGY

Bus Coupler-A Function with 2 CT:

Case 1:-

Fault fed from BUS 1A to BUS2A via Bus coupler-A

.  BB1A                                                                                                                                                                                     DISCONNECTOR ON

.

BB2A                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

305                                  105                                          T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                       130

D03                            D01                                      D130

Faulty busbar trips immediately (Bus-2A & D01)            16   ms

Case 2:-

Fault fed from BUS2A to BUS1A via Bus coupler-1

.  BB1A                                                                                                                                                                                     DISCONNECTOR ON

.

BB2A                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

105                                     305                                         T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                       130

D01                          D03                                          D130

Faulty busbar trips immediately (Bus-1A & D01)           16   ms

INTERNAL FAULT IN BUS COUPLER

Case 1:-

No current passing in T2 of Bus coupler.

.  BB1A                                                                                                                                                                                     DISCONNECTOR ON

.

BB2A                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

305                                       107                                                                 T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                         130

D03                          D01                                           D130

Faulty Busbar B/C1A & B/C 2A trips immediately          16    ms

Faulty Busbar D03 trips after Delay                              84      ms

Case 2:-

No current passing in T1 of Bus coupler.

.  BB1A                                                                                                                                                                                     DISCONNECTOR ON

.

BB2A                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

105                                       307                                                                 T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                       130

D01                           D03                                             D130

Faulty Busbar B/C1A & B/C2A trips immediately          16       ms

Faulty Busbar D03 trips after time delay                        77       ms

TESTING OF EXTERNAL FAULT

Bus coupler with 2 CT:

Case 1:

.  BB1A                                                                                                                                                                                     DISCONNECTOR ON

.

BB2A                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

105                                       307                                                                 T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                       130

D01                                   D03                                D130

No TRIP (Stable condition)   OK

Case 2:

.  BB1A                                                                                                                                                                                     DISCONNECTOR ON

.

BB2A                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

105                                       307                                                      T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                       130

D01                              D03                                            D130

No TRIP (Stable condition)     OK

BUS COUPLER-B FUNCTION WITH 2 CT:

Case 1:-

Fault fed from BUS 1B to BUS2B via Bus coupler-B

.  BB1B                                                                                                                                                                                     DISCONNECTOR ON

.

BB2B                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

205                                  405                                                                  T1                        T2                                                     FAULT LOCATION

.                           T1                                         T1                                            230

D02                            D04                                      D230

Faulty busbar trips immediately (Bus-2B & D04)            16   ms

Case 2:-

Fault fed from BUS2A to BUS1A via Bus coupler-1

.  BB1B                                                                                                                                                                                     DISCONNECTOR ON

.

BB2B                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

405                                     205                                         T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                       230

D04                          D02                                         D230

Faulty busbar trips immediately (Bus-1A & D04)           16   ms

INTERNAL FAULT IN BUS COUPLER

Case 1:-

No current passing in T2 of Bus coupler.

.  BB1B                                                                                                                                                                                     DISCONNECTOR ON

.

BB2B                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

405                                       207                                         T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                         130

D04                          D02                                           D230

Faulty Busbar B/C1B & B/C 2B trips immediately          16    ms

Faulty Busbar D04 trips after Delay                              84      ms

Case 2:-

No current passing in T1 of Bus coupler.

.  BB1B                                                                                                                                                                                     DISCONNECTOR ON

.

BB2B                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

205                                      405                                         T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                       230

D02                           D04                                             D130

Faulty Busbar B/C1B & B/C2B trips immediately          16       ms

Faulty Busbar D04 trips after time delay                        77       ms

TESTING OF EXTERNAL FAULT

Bus coupler with 2 CT:

Case 1:

.  BB1B                                                                                                                                                                                     DISCONNECTOR ON

.

BB2B                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

205                                       405                                         T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                       230

D02                                   D04                                D230

No TRIP (Stable condition)   OK

Case 2:

.  BB1B                                                                                                                                                                                     DISCONNECTOR ON

.

BB2B                                                                                                                                                                                      DISCONNECTOR OFF

.                                                                                                                                                           CIRCUIT BREAKER ON

.      Q1                   Q2                Q1                Q2                               Q1                     Q2                                                     CT LOCATION

.                                                                                                                                                          CURRENT FLOW PATH

.

205                                       405                                         T1                        T2                                                     FAULT LOCATION

.                         T1                                      T1                                       230

D02                              D04                                            D230

No TRIP (Stable condition)     OK

BUS SECTION FUNCTION WITH 2 CT

Condition A

Fault fed from BUS1A to BUS1C via Bus section

.  BB1A                                                                                                                                               BB1C                            DISCONNECTOR ON

.	         DISCONNECTOR OFF

.  BB2A                                                                                                                                                BB2C                           CIRCUIT BREAKER ON

.                                                                                                                                                            CT LOCATION

.                                                                                                                                                                                                   CURRENT FLOW DIRECTION

.     Q1              Q2                                                        Q1                Q2                      Q1                Q2                                    FAULT LOCATION

.

T 1                 T2

.                                                                                        B/S

.         105                                                                                                                                          206

.

BUS SECTION

.          T1                                                                                                                            T1

.

.     D01                                                                                                D02

Faulty busbar trips immediately (B/S-1B & D02)     15         ms

Condition B

Fault fed from BUS1C to BUS1A via Bus section

.  BB1A                                                                                                                                               BB1C                            DISCONNECTOR ON

.	         DISCONNECTOR OFF

.  BB2A                                                                                                                                                BB2C                           CIRCUIT BREAKER ON

.                                                                                                                                                            CT LOCATION

.                                                                                                                                                                                                   CURRENT FLOW DIRECTION

.     Q1              Q2                                                        Q1                Q2                      Q1                Q2                                    FAULT LOCATION

.

T1                 T2

.                                                                                        B/S

.         105                                                                                                                                         205

.

BUS SECTION

.          T1                                                                                                                            T1

.        D01                                                                                                D02

Faulty busbar trips immediately (Bus-1A & D01)    16        ms

INTERNAL FAULT IN BUS SECTION BETWEEN 2 CT’s

No current passing in T2 of Bus section.

.  BB1A                                                                                                                                               BB1C                            DISCONNECTOR ON

.	         DISCONNECTOR OFF

.  BB2A                                                                                                                                                BB2C                           CIRCUIT BREAKER ON

.                                                                                                                                                            CT LOCATION

.                                                                                                                                                                                                   CURRENT FLOW DIRECTION

.     Q1              Q2                                                        Q1                Q2                      Q1                Q2                                    FAULT LOCATION

.

T 1                 T2

.                                                                                         B/S

.       105                                                                                                                                         2205

.

BUS SECTION

.          T1                                                                                                                            T1

.

.       D105                                                                                           D205

Faulty Busbar trips immediately        B/S-1A& B/S-1B                 15    ms

Faulty Busbar Trips Delayed 	     D02                                   80   ms

No current passing in T1 of Bus section .

.  BB1A                                                                                                                                               BB1C                            DISCONNECTOR ON

.	         DISCONNECTOR OFF

.  BB2A                                                                                                                                                BB2C                           CIRCUIT BREAKER ON

.                                                                                                                                                            CT LOCATION

.                                                                                                                                                                                                   CURRENT FLOW DIRECTION

.     Q1              Q2                                                        Q1                Q2                      Q1                Q2                                    FAULT LOCATION

.

T1                 T2

.                                                                                        B/S

.       A605                                                                                                                                         A606

.

BUS SECTION

.          T1                                                                                                                            T1

.     D01                                                                                                D02

Faulty Busbar trips immediately        B/S-1A& B/S-1B                 15    ms

Faulty Busbar Trips Delayed 	     D01                                   80   ms

TESTING OF EXTERNAL FAULT WITH BUS SECTION CLOSED

Condition A

.  BB1A                                                                                                                                               BB1C                            DISCONNECTOR ON

.	         DISCONNECTOR OFF

.  BB2A                                                                                                                                                BB2C                           CIRCUIT BREAKER ON

.                                                                                                                                                            CT LOCATION

.                                                                                                                                                                                                   CURRENT FLOW DIRECTION

.     Q1              Q2                                                        Q1                Q2                      Q1                Q2                                    FAULT LOCATION

.

T 1                 T2

.                                                                                        B/S

.       105                                                                                                                                            205

.

BUS SECTION

.          T1                                                                                                                            T1

.

.      D01                                                                                                  D02

No Trip (Stable condition)   OK

Condition B

.  BB1A                                                                                                                                               BB1C                            DISCONNECTOR ON

.	         DISCONNECTOR OFF

.  BB2A                                                                                                                                                BB2C                           CIRCUIT BREAKER ON

.                                                                                                                                                            CT LOCATION

.                                                                                                                                                                                                   CURRENT FLOW DIRECTION

.     Q1              Q2                                                        Q1                Q2                      Q1                Q2                                    FAULT LOCATION

.

T1                 T2

.                                                                                        B/S

.       105                                                                                                                                            206

.

BUS SECTION

.          T1                                                                                                                            T1

.         D01                                                                                                 D02

No Trip (Stable condition)    OK

TESTING OF Internal FAULT WITH BUS SECTION-2 isolators CLOSED

.  BB2A                                                                                                                                               BB2B                            DISCONNECTOR ON

.	         DISCONNECTOR OFF

.  BB1A                                                                                                                                                BB1B                           CIRCUIT BREAKER ON

.                                                                                                                                                            CT LOCATION

.                                                                                                                                                                                                   CURRENT FLOW DIRECTION

.     Q2              Q1                                                        Q1                Q2                      Q2                Q1                                   FAULT LOCATION

.

T 1                 T2

.       105                                                                                                                                            205

.

BUS SECTION

.          T1                                                                                                                            T1

.

.      D01                                                                                                  D02

Busbar Trips all connected bays instantaneously ( D01 & D02 ).    16 ms