|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. GENERAL DATA AND INFORMATION:

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Panel No. | **RB.UV** |  | Designation | U05.5001(27UV1) |
| Serial No. | **1VHR91083763** | Rated Voltage | 125 VDC |
| Make |  | Aux. Voltage | 48 – 250 VAC/DC |
| DWG. & SH. No. | CD-268544 | Frequency | 50 – 60 Hz |
| VT Ratio | 132000/115V |  |  |

2. MECHANICAL CHECKS AND VISUAL INSPECTION:

|  |  |  |
| --- | --- | --- |
| ITEM | DESCRIPTION | CHECKED |
| 1 | Inspect for physical damage / defects. |  |
| 2 | Verify Connections as per approved drawings. |  |
| 3 | Check tightness of all connections. |  |
| 5 | Check apparatus lists. |  |
| 6 | Check ferrules |  |
| 7 | Test Switch checked for correct function. |  |
| 8 | Check case earthing. |  |

3. ELECTRICAL TESTS: With relay energized condition

|  |  |  |
| --- | --- | --- |
| ITEM | DESCRIPTION | CHECKED |
| 1 | Measured auxiliary supply. |  |
| 2 | Clock set at local time. |  |
| 3 | Time maintained when auxiliary supply removed. |  |
| 5 | Relay healthy (green) LED working. |  |
| 6 | Trip (red) LED working. |  |

3.1 OPERATING DC SUPPLY CURRENT:

|  |  |  |  |
| --- | --- | --- | --- |
| DC Volt (V) | DC CurrentWithout Fault (mA) | DC CurrentDuring Fault (mA) | Calculated WATT (W) |
| 125 VDC |  |  |  |

**(Relays /energized):** < 12.0 W (**nominal**)/< 18.0 W (**max**) Technical Data page: 8094. INPUTS AND OUTPUTS TESTS:**INPUT OPTO-ISOLATORS CHECKS (With Relay Energized):** Test Procedure: Go to CONFIGURATION - MONITORING, I/O STATUS, then go to BINARY INPUTS VALUES ( X120 (AIM) – X110 (BIO) )to check the values after giving pulse on each BI.

|  |  |  |  |
| --- | --- | --- | --- |
| **OPTO INPUT NO.** | **TEST METHOD****(Energize only one at a time with** **125V DC Station Battery voltage)** | **RESULT****Display FALSE to TURE** | **REMARKS** |
| **X110** |
| BI 1 | ENERGIZE TB NO. X110 : 1 – 2 |  | **SPARE** |
| BI 2 | ENERGIZE TB NO. X110 : 3 – 4 |  | **SPARE** |
| BI 3 | ENERGIZE TB NO. X110 : 5 – 6C |  | **SPARE** |
| BI 4 | ENERGIZE TB NO. X110 : 7 – 6C |  | **SPARE** |
| BI 5 | ENERGIZE TB NO. X110 : 8 – 9C |  | **SPARE** |
| BI 6 | ENERGIZE TB NO. X110 : 10 – 9C |  | **SPARE** |
| BI 7 | ENERGIZE TB NO. X110 : 11 – 12C |  | **SPARE** |
| BI 8 | ENERGIZE TB NO. X110 : 13 – 12C |  | **SPARE** |
| **X120** |
| BI 1 | ENERGIZE TB NO. X120 : 1 – 2C |  | **SPARE** |
| BI 2 | ENERGIZE TB NO. X120 : 3 – 2C |  | **SPARE** |
| BI 3 | ENERGIZE TB NO. X120 : 4 – 2C |  | **SPARE** |
| BI 4 | ENERGIZE TB NO. X120 : 5 – 6 |  | **SPARE** |
| **X130** |
| BI 1 | ENERGIZE TB NO. X130 : 1 – 2 |  | **SPARE** |
| BI 2 | ENERGIZE TB NO. X130 : 3 – 4 |  | **SPARE** |
| BI 3 | ENERGIZE TB NO. X130 : 5 – 6 |  | **SPARE** |
| BI 4 | ENERGIZE TB NO. X130 : 7 – 8 |  | **SPARE** |

**OUTPUT RELAYS CHECKS (With Relay Energized):**Test Procedure: Go to IED CONFIGURATION, TESTS, IED TEST, TEST MODE : ON, then go to BINARY OUTPUTS-CHANGE THE POSITION OF EACH BO FROM FULSE TO TURE FROM HMI,then check contact resistance.

|  |  |  |  |
| --- | --- | --- | --- |
| **OUTPUT RELAY No.** | **TEST METHOD****(Energize only one relay at a time by****Test ON in ‘IED TEST’)** | **RESULT****Contact Checked****≤ 0.2Ω** | **REMARKS** |
| **X100** |
| PO1 | CONTACT OPERATED X100 : 6 – 7 (N/O) |  | **UV OPTD (STG-1)** |
| PO2 | CONTACT OPERATED X100 : 8 – 9 (N/O) |  | **UV OPTD (STG-2)** |
| SO1 | CONTACT OPERATED X100 : 10 – 11 /10 - 12 (C/O) |  | SPARE |
| SO2 | CONTACT OPERATED X100 : 13 – 14 (N/O) |  | SPARE |
| PO3 | CONTACT OPERATED X100 : 16 – 17 (N/O) |  | **UV OPTD (STG-3)** |
| PO4 | CONTACT OPERATED X100 : 21 – 22 (N/O) |  | **UV OPTD (FR)** |
| IRF | CONTACT OPERATED X100 : 3 – 4 (N/O) |  | WATCHDOG |
| **X110** |
| SO1 | CONTACT OPERATED X110 : 14 – 16 /14 - 15 (C/O) |  | SPARE |
| SO2 | CONTACT OPERATED X110 : 17 – 19 /17 - 18 (C/O) |  | SPARE |
| SO3 | CONTACT OPERATED X110 : 20 – 22 /20 - 21 (C/O) |  | SPARE |
| SO4 | CONTACT OPERATED X110 : 23 – 24 (N/O) |  | SPARE |

**INDICATION LED TEST****LED Checks:**Go to MONITORING,PROGRAMMABLE LEDS to view the physical position of the LED.

|  |  |  |
| --- | --- | --- |
| **OPTO Input Number** | **Result Display On or Off** | **Function** |
| LED 1 |  | **UV OPTD (STG-1)** |
| LED 2 |  | **UV OPTD (STG-2)** |
| LED 3 |  | **UV OPTD (STG-3)** |
| LED 4 |  | **DIST. TRIGGERED**  |
| LED 5 |  | SPARE |
| LED 6 |  | SPARE |
| LED 7 |  | SPARE |
| LED 8 |  | SPARE |

5. MEASUREMENTS ACCURACY CHECKS:

|  |  |  |
| --- | --- | --- |
| Applied Value | Expected Value ( A ) | Displayed value ( A ) |
| R | Y | B  |
| 10 | 19.88 kV |  |  |  |
| 30 | 59.64 kV |  |  |  |
| 50 | 99.4 kV |  |  |  |
| 66.4 | 132.0 kV |  |  |  |

**6. UNDERVOLTAGE PROTECTION (27) PICK UP & DROP OFF :**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Voltage****Setting** | **Expected****Voltage (V)** | **Operate Voltage** | **Reset** **Voltage** | **Ratio (Operate/Reset)** |
| **0.9 Un** | **59.75**  |  |  |  |
| **0.7 Un** | **46.5**  |  |  |  |
| **0.5 Un** | **33.19**  |  |  |  |
| **0.3 Un** | **19.92**  |  |  |  |

|  |  |  |  |
| --- | --- | --- | --- |
| **Voltage** **Setting** | **Operate** **Time Setting (ms)** | **Expected****Time (ms)** | **Operate Time (ms)** |
| **0.9 Un** | **60** |  |  |
| **90** |  |  |
| **150** |  |  |

|  |  |  |  |
| --- | --- | --- | --- |
| **Voltage** **Setting** | **Voltage****Blocking Setting (ms)** | **Expected****Voltage (ms)** | **Operate Time (ms)** |
| **0.9 Un** | **0.2 Un** | **13.28** |  |
| **0.3 Un** | **19.92** |  |

**Limits:**I > Pick-up: Setting ±5% or 20 mAI > Drop-off: 100%of setting ±5% or 20 mATimers: ± 2% or 50 ms whichever is greater to manual page : 26/

|  |  |  |
| --- | --- | --- |
| 1 | Communication with PC |  |
| 2 | Event Record Check |  |
| 3 | Disturbance Record Check |  |

 |