## MACHING FACOTR
MATCHING FACTOR CALCULATION
HV MVA | 100
LV MVA | 100
HV VT | 132000
LV VT | 33000
HV CTR | 800
LV CTR | 2000
I RATED HV | 437.3868
I RATED LV | 1749.5471
MATCHING FACTOR HV | 1.829
MATCHING FACTOR LV | 1.1432

## SLOPE CALC
SLOPE - 1 FOR DIFFERENTIAL
HV | LV | FACTOR HV | FACTOR LV | I DIFF CALC | I BIAS CALC | K1 SETTING | K1 CALCULATED | I DIFF MEASURED | I BIAS MEASURED
1.5 | 1.7751 | 1.83 | 1.143 | 0.71609 | 2.387 | 0.3 | 30.5764 | 0.714 | 2.397
2 | 2.3668 | 1.83 | 1.143 | 0.95478 | 3.1826 | 0.3 |  | 0.958 | 3.195
SLOPE - 2
HV | LV | FACTOR HV | FACTOR LV | I DIFF CALC | I BIAS CALC | IS2 | K1 SETTING | K2 SETTING | K2 CALCULATED | I DIFF MEASURED | I BIAS MEASURED
5 | 4.6807 | 1.83 | 1.143 | 3.8 | 7.25 | 4 | 0.3 | 0.8 | 80.1375 | 3.82 | 7.276
6 | 5.3668 | 1.83 | 1.143 | 4.8457 | 8.5571 | 4 | 0.3 | 0.8 |  | 4.869 | 8.585
FOR REF USE MATCHING FACTOR = 1